## 0. Abbreviations
0. | List of abbreviations
| Physical units | Measurement size
°C | degrees Celsius | Temperature
a | Year (annum in Latin) | time
a* | Heating season | time
BW | Biotope value unit | Biotope value
cm | Centimeter | Length
d | day | time
EUR | Euro | Currency
h | hour | time
K | Kelvin | Temperature
kg | Kilogram | Mass
kW | Kilowatt | Output
kWh | Kilowatt-hour | Energy
l | Liter | Volume
lux | lux | Illuminance
m | Meter | Length
m² | Square meter | Area
m³ | Cubic meter | Volume
min | Minute | time
MWh | Megawatt-hour | Energy
N | Usage | Number
P | Persons | Number
s | Second | time
Sp | Flushes | Number
to | Ton | Mass
| Physical parameters | Unit
A | Area | m²
alfa | Heat transmission | W/m²K
bZ | Operating time circulation | h/d
ERA | Energy reference area | m²
fb | Shading factor | -
fe | Usage factor electrical | -
fr | Share of window frame | -
g | Overall degree of energy transmissivity | -
HGT | Heating degree days | Kd/a*
HT | Number of heating days | d/a*
k | Heat transmissivity | W/m²K
k* | Heat transmissivity | W/mK
lam | Heat conductivity | W/mK
s | Layer thickness | cm
sig | Siegert's formula | 1/K
T | Temperature | K
V | Volume | m³

## 1. Total cost
1a) | Usage duration, cost of |  | Usage
Maintenance + servicing
| (based on HMULF 1999 / VDI 2067) |  | (Years)
| Entire building |  | 40
| Insulation |  | 25-30
| Windows |  | 15-30
| Venetian blinds, roller shutters |  | 15-20
| Heating/cooling | < 300 kWt | 15
| Generation | > 300 kWt | 15
| Cogeneration unit | > 100 kWe | 15
|  | > 500 kWe | 15
| Heat recovery |  | 15
| Control |  | 10
| Thermostat valves |  | 15
| Radiator, heat distribution |  | 25
| District heat lines |  | 30
| Ventilation systems |  | 15
| Air conditioners |  | 15
| Lighting systems |  | 15
| Other technical systems |  | 15
| Other construction systems |  | 30
2a) | Annuity factors |  |  |  | Capital interest
| Usage duration (a) | 4% | 5% | 6% | 7% | 8% | 9% | 10%
| 1 | 1.04 | 1.05 | 1.06 | 1.07 | 1.08 | 1.09 | 1.1
| 2 | 0.5302 | 0.5378 | 0.54544 | 0.55309 | 0.56077 | 0.56847 | 0.57619
| 3 | 0.36035 | 0.36721 | 0.37411 | 0.38105 | 0.38803 | 0.39505 | 0.40211
| 5 | 0.22463 | 0.23097 | 0.2374 | 0.24389 | 0.25046 | 0.25709 | 0.2638
| 10 | 0.12329 | 0.1295 | 0.13587 | 0.14238 | 0.14903 | 0.15582 | 0.16275
| 15 | 0.089941 | 0.096342 | 0.10296 | 0.10979 | 0.11683 | 0.12406 | 0.13147
| 20 | 0.073582 | 0.080243 | 0.087185 | 0.094393 | 0.10185 | 0.10955 | 0.11746
| 25 | 0.064012 | 0.070952 | 0.078227 | 0.085811 | 0.093679 | 0.10181 | 0.11017
| 30 | 0.05783 | 0.065051 | 0.072649 | 0.080586 | 0.088827 | 0.097336 | 0.10608
| 40 | 0.050523 | 0.058278 | 0.066462 | 0.075009 | 0.08386 | 0.09296 | 0.10226
| 50 | 0.04655 | 0.054777 | 0.063444 | 0.07246 | 0.081743 | 0.091227 | 0.10086
| 100 | 0.040808 | 0.050383 | 0.060177 | 0.070081 | 0.080036 | 0.090016 | 0.10001
3a) | 1: Cleaning costs; 1.05: Costs
€/m2
| School cleaning, smooth surfaces/month |  | 1
Windows
| Glass (per cleaning, twice annually) |  | 0.39
| Glass with crane lift (per cleaning, twice annually) |  | 0.75
| Glass (per cleaning, once annually) |  | 0.34

## 2. Building components
A. | Plaster, mortar | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
| Screed | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Loam | 1800 | 0.93 | 480 | 2-5 | 0-30 | no | no | conditionally
| Gipsum plaster (pure) | 1200 | 0.35 | 280 | 10 | 465 | conditionally | conditionally | no
| Gipsum mortar (with sand) | 1400 | 0.7 | 325 | 10 | 160 | conditionally | conditionally | no
| Cement | 2000 | 1.4 | 560 | 15-35 | 265 | conditionally | no | yes
| Polystyrene insulating plaster | 350 | 0.07 | 100 | 5 | 265 | conditionally | conditionally | no
| Synthetic resin plaster | 1100 | 0.7 | 440 | 50-200 |  | yes | conditionally | no
| Cement screed | 2000 | 1.4 | 560 | 15-35 | 235 | conditionally | no | yes
B. | Concrete and | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
| light concrete | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Normal concrete B I | 2400 | 2.1 | 670 | 70-150 | 2770 | conditionally | no | yes
| Normal concrete B II | 2400 | 2.1 | 670 | 100-150 | 3200 | conditionally | no | yes
| light concrete | 1800 | 1.3 | 505 | 100 | 1010 | conditionally | conditionally | yes
| Aerated concrete prefab component | 600 | 0.19 | 170 | 5-10 | 625 | conditionally | no | yes
C. | Construction panels | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
| cladding | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Cement fiber plates | 2000 | 0.6 | 560 | 50 |  | conditionally | conditionally | no
| Gypsum board | 900 | 0.21 | 270 | 8 | 760 | conditionally | conditionally | no
| Light wood-wool boards | 360 | 0.093 | 210 | 2-5 |  | no | no | conditionally
| Wood fiber plate | 1000 | 0.17 | 580 | 70 | 650 | conditionally | yes | conditionally
| Particleboard, synthetic resin | 800 | 0.17 | 350 | 50-140 | 800 | conditionally | yes | conditionally
| Particleboard, glued | 1250 | 0.2 | 485 |  | 800 | conditionally | no | conditionally
| Plywood | 800 | 0.15 | 350 | 50-400 |  | conditionally | conditionally | conditionally
| Solid wood | 600 | 0.13 | 350 | 40 | 470 | no | no | yes
D. | Wall construction materials | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
|  | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Solid loam | 1800 | 0.93 | 505 | 2-3 | 0-25 | no | no | yes
| Light loam | 800 | 0.25 | 220 | 2 | 0-30 | no | no | yes
| Bricks | 2000 | 0.96 | 560 | 50-100 | 1750 | conditionally | no | yes
| Light air bricks | 1000 | 0.45 | 260 | 5-10 | 1040 | conditionally | no | yes
| Porous air bricks | 700 | 0,1-0,16 | 180 | 4 | 595 | yes | conditionally | yes
| Solid calcium silicate | 2000 | 1.1 | 520 | 10-25 | 435 | conditionally | no | yes
| Calcium silicate stone, perforated | 1400 | 0.7 | 365 | 5-10 | 340 | conditionally | no | yes
| Aerated concrete stone G4 | 800 | 0.29 | 230 | 5-10 | 720 | conditionally | no | conditionally
| Aerated concrete stone G6 | 500 | 0.22 | 145 | 5-10 | 540 | conditionally | no | conditionally
| Light concrete Hbl 6 | 1200 | 0.6 | 335 | 5-10 | 200 | conditionally | no | yes
| Light concrete Hbl 4 | 700 | 0.35 | 200 | 5-10 | 200 | conditionally | no | yes
| Solid pumice | 600 | 0.22 | 170 | 5-10 | 180 | conditionally | no | yes
E. | Insulation materials | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
|  | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Wood fiber plate (porous) | 200 | 0.045 | 100 | 5 |  | no | no | no
| Coconut fibers (mats) | 75 | 0.04 | 16 | 1 |  | no | no | yes
| Baked cork insulation plates | 120 | 0.045 | 62 | 10 |  | conditionally | conditionally | no
| Mineral fibers | 80 | 0.04 | 32 | 1 | 270 | yes | yes | no
| Foam glass DIN 18 174 | 130 | 0.05 | 30 | 1000 | 320 | conditionally | no | yes
| PU local insulation | 30-60 | 0.03 | 15-23 | 30-100 | 1585 | yes | conditionally | no
| PUR, closed cells | 30 | 0.025 | 12 | 30-100 | 1585 | yes | conditionally | no
| PS particle foam | 30 | 0.035 | 12 | 30-70 | 695 | yes | conditionally | no
| PS extruder foam | 40 | 0.035 | 16 | 80-300 | 695 | yes | conditionally | no
| Cellulose insulation | 35-60 | 0.045 | 25-40 | 1-1,5 | ca. 50 | no | no | yes
F. | Windows and glass | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
|  | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Coniferous timber (spruce) | 600 | 0.13 | 350 | 40 | 470 | conditionally | no | yes
| Oak/beech | 800 | 0.2 | 370 | 80 | 750 | yes | no | yes
| PVC | 1500 | 0.19 |  | 600-1200 | 22000 | yes | yes | conditionally
| Aluminum | 2700 | 200 | 675 | dense | 195500 | yes | no | yes
| Steel | 7500 | 58 | 975 | dense | 70000 | yes | no | yes
| Window glazing | 2500 | 0.8 | 575 | 100000 | 14750 | yes | no | yes
| Acrylic glass | 1180 | 0.19 | 485 | 100000 |  | conditionally | no | yes
G. | Timber and | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
| Composite wood | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Coniferous timber (spruce) | 600 | 0.13 | 350 | 40 | 470 | conditionally | no | yes
| Oak/beech | 800 | 0.2 | 460 | 40 | 750 | yes | no | yes
| Glued layered timber | 600-800 | 0.2 | 460 | 50 | 1150 | conditionally | conditionally | yes
| Plywood (DIN 68 705) | 800 | 0.15 | 350 | 50-400 |  | conditionally | conditionally | conditionally
| Wood particle board | 700 | 0.13 | 400 | 50-100 | 800 | conditionally | conditionally | no
| Hard wood-fiber boards | 1000 | 0.17 | 580 | 70 | 650 | conditionally | yes | conditionally
H. | Ceramics and | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
| natural stone | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m³) | Manufacture | Usage
| Stone tiling | 2000 | 1 | 510 | 100-200 | 1400 | yes | no | no
| Porcelain | 2300 | 0.9 | 600 | 100000 | 1400 | yes | no | no
| Granite, syenite | 2600-2800 | 3.5 | 720 | 100-150 |  | conditionally | no | yes
| Basalt, melaphyre | 3000-3150 | 3.5 | 775 | 100-150 |  | conditionally | no | yes
| Pumice | 350-1550 | 0.19 | 280 | 5-10 |  | conditionally | no | yes
| Shale | 2700-2800 | 2 | 680 | 25 |  | conditionally | no | yes
| Marble | 2600-2800 | 1.2 | 700 | 50-100 |  | conditionally | no | yes
| Sandstone | 2400 | 2.1 | 600 | 50-100 |  | conditionally | no | yes
| Limestone | 2400-2500 | 2.3 | 625 | 50-100 |  | conditionally | no | yes
I. | Sealants and | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
| sealing tracts | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m²) | Manufacture | Usage
| Mastic asphalt | 2000 | 0.7 | 520 | >1500 | 18 | yes | conditionally | yes
| Bitumen, cold 1-2mm | 1100 | 0.17 | 515 | 4-8 | 1.2 | yes | conditionally
| Bitumen, hot 2-5mm | 1100 | 0.17 | 515 | 24-60 | 5 | yes | conditionally
| PVC-P 1.2-2.4 mm |  |  |  | 12-30 | 52 | yes | yes | conditionally
| EPDM + 1.3-2.5 mm |  |  |  | 40
| ECB + 1.0-3.0 mm |  |  |  | 80-180 | 35 | yes | conditionally | no
K. | Roofing and | Thickness | Heat transmissivity | Heat storage | Steam diffusion | Primary energy | Pollutants | Pollutants | Recycling
| metals | (kg/m³) | (W/mK) | (Wh/m³K) | (-) | (kWh/m²) | Manufacture | Usage
| Shale | 2700 | 0.2 | 680 | 25 |  | no | no | conditionally
| Cement fiber plates | 2000 | 0.6 | 560 | 20-50 |  | conditionally | conditionally | no
| Roof tiles (unglazed) | 1800 | 0.81 | 470 | 8 | 1150 | conditionally | no | yes
| Concrete roof stones | 2400 | 2.1 | 638 | 35 | 500 | conditionally | no | yes
| Galvanized steel sheeting | 7500 | 58 | 975 | dense | 70000 | yes | conditionally | conditionally
| Aluminum sheeting | 2700 | 203 | 673 | dense | 195000 | yes | conditionally | yes
| Copper sheeting | 8900 | 383 | 986 | dense |  | yes | conditionally | yes
Source: Leitfaden Umweltschutz im Bauwesen des Landes Hessen, HMDF 1991
2b) | Heat transmissivity resistance |  | Ri | Ra
| (DIN 4701 part 2) |  | (m²K/W) | (m²K/W)
| Walls |  | 0.13 | 0.04
Floors/ceilings:
| Heat from bottom to top |  | 0.13 | 0.04
| Heat from top to bottom |  | 0.17 | 0.04
| Cavities, curtain façade |  |  | 0.09

## 3. Cost
3a) | Usage duration, cost of |  | Maintenance +
| Maintenance + servicing |  | servicing
| (based on HMULF 1999 / VDI 2067) |  | (%/a)
| Entire building |  | 1.5
| Insulation |  | 1
| Windows |  | 1.5
| Venetian blinds, roller shutters |  | 4
| Heating/cooling | < 300 kWt | 3.5
| Generation | > 300 kWt | 3
| Cogeneration unit | > 100 kWe | 6
|  | > 500 kWe | 4
| Heat recovery |  | 4
| Control |  | 3
| Thermostat valves |  | 3
| Radiator, heat distribution |  | 1.5
| District heat lines |  | 2
| Ventilation systems |  | 3.5
| Air conditioners |  | 4-5
| Lighting systems |  | 1.5
| Other technical systems |  | 1.5
| Other construction systems |  | 1
3b) | Specific cost (net) |  |  | (All costs including installation and related work)
300 | Building - construction design |  |  |  |  | As of | 2011-01-24
310 | Excavation
320 | Foundation: foundations
330 | Outer walls
| Scaffolding, EIFS polystyrene, thermal conductivity group 035 with 18 cm, exterior plaster |  |  |  |  | 105 | €/m²
| Frame, EIFS mineral wool, thermal conductivity group 035 with 18 cm, exterior plaster |  |  |  |  | 120 | €/m²
| Scaffolding, EIFS hard foam, thermal conductivity group 022 with 10 cm, exterior plaster |  |  |  |  | 120 | €/m²
| Additional cost of reinforcement EIFS EPS (polystyrene) thermal conductivity group 035 per cm |  |  |  |  | 1.8 | €/m²
| Additional cost of reinforcement EIFS mineral wool thermal conductivity group 035 per cm |  |  |  |  | 2.9 | €/m²
| Additional cost of reinforcement EIFS hard foam thermal conductivity group 022 per cm |  |  |  |  | 4.9 | €/m²
| Additional cost EIFS 180 mm EPS 035 over new plaster |  |  |  |  | 45 | €/m²
| Scaffolding, curtain façade polystyrene thermal conductivity group 035 with 18 cm, façade plates |  |  |  |  | 130 | €/m²
| Evacuated panels, 20 mm thick, lambda = 0.005 W/mK |  |  |  |  | 60-80 | €/m²
| Installation of wood/aluminum windows with insulated double glazing (Uw=1.4 W/m²K) |  |  |  |  | 350-400 | €/m²
| Installation of wood/aluminum windows with insulated triple glazing (Uw=0.8 W/m²K) |  |  |  |  | 390-450 | €/m²
| Installation or replacement of shading with daylighting function (external aluminum blinds) |  |  |  |  | 150 | €/m²
| Internal insulation with 120 mm of mineral insulation thermal conductivity group 045 and plaster |  |  |  |  | 55 | €/m²
| Additional cost of reinforced mineral insulation plates thermal conductivity group 045 per cm |  |  |  |  | 2 | €/m²
| Removal of old plaster, new plaster with 3x3 cm mineral insulation plaster thermal conductivity group 065 |  |  |  |  | 60 | €/m²
340 | Interior walls
350 | Ceilings
| Installation of basement ceiling from below with 120 mm polystyrene thermal conductivity group 035, leveling |  |  |  |  | 30 | €/m²
| Additional cost of insulation reinforcement per centimeter |  |  |  |  | 1.5 | €/m²
| Insulation above ceiling with 220 mm mineral thermal conductivity group 035 (10 percent walkable) |  |  |  |  | 25 | €/m²
| Additional cost of insulation reinforcement per centimeter |  |  |  |  | 1 | €/m²
360 | Roofs
| Flat roof: Sloped mineral fiber insulation, 260 mm on average, bitumen rows |  |  |  |  | 85 | €/m²
| Additional cost of insulation reinforcement per centimeter |  |  |  |  | 1.2 | €/m²
| Additional cost of flat roof insulation (extra routing) 260 mm above simple sealing |  |  |  |  | 35 | €/m²
| Roof sealing for photovoltaics |  |  |  |  | 220 | €/m²
| Insulation between rafters from inside (140 mm mineral wool, gypsum board) |  |  |  |  | 50 | €/m²
| Insulation between and below rafters from inside (260 mm mineral wool, gypsum board) |  |  |  |  | 65 | €/m²
370 | - 390 Other building designs
400 | Building – building services
410 | Sewage, water, and gas systems
| Installation of water-saving aerator 5-6 l/min |  |  |  |  | 12 | €/h
| Self-closing faucets 5-6 l/min, switch off after 5 s |  |  |  |  | 50 | €/h
| Water-conserving showerhead 7 l/min |  |  |  |  | 120 | €/h
| Stop function for toilet tank added (weight) + label |  |  |  |  | 15 | €/h
| Rainwater cistern including pipes and domestic water connection |  |  |  |  | 1000 | €/m³
420 | Heating systems
| Renovation of central heater (condensation boiler, distribution, controls) |  |  |  |  | 500 | €/kW
| Boiler replacement (condensation, gas) |  |  |  |  | 100 | €/kW
| Cogen including noise prevention, Kat., electric cabinet, aeration and deaeration |  |  |  | 5,783*Pel-0,3875 |  | €/kW
| Pellet boiler including tank, delivery, controls, chimney (100 kW) |  |  |  |  | 375 | €/kW
| Pellet boiler including tank, delivery, controls, chimney (15 kW) |  |  |  |  | 650 | €/kW
| New energy-efficient circulation pumps (up to 100 W) |  |  |  |  | 250 | €/unit
| Downhole heat exchanger (ca. 50 W/m output) |  |  |  |  | 900 | €/kW
| Solar thermal array including storage, pipes, control system (10-20 m²) |  |  |  |  | 650-700 | €/m²
| Solar thermal array including storage, pipes, control system (> 50 m²) |  |  |  |  | 350-480 | €/m²
| Control for existing heating circuit (pump, mixed valve, controls) |  |  |  |  | 2000 | €/unit
| New thermostat valves |  |  |  |  | 60 | €/unit
430 | Air handling systems
| Ventilation unit of passive house quality with two ventilators and heat recovery (ca. 1,000 m³/h) |  |  |  |  | 3 | €/m³
| Ventilation unit of passive house quality with two ventilators and heat recovery (ca. 5,000 m³/h) |  |  |  |  | 1.5 | €/m³
| New building, ventilation fresh and extract air including heat recovery and ducts (ca. 2.500 m³/h) |  |  |  |  | 20 | €/m³
| New building, ventilation fresh and extract air including heat recovery and ducts (ca. 5.000 m³/h) |  |  |  |  | 15 | €/m³
| Variable-frequency drive for motor output > 30 kW |  |  |  |  | 150 | €/kW
| Variable-frequency drive for motor output > 3 kW |  |  |  |  | 350 | €/kW
440 | Three-phase current systems
| Preparation for parabolic lamp 1x58W with ballast |  |  |  |  | 70 | €/unit
| Renovation of lighting in offices and schools (300 lux, parabolic lamps with ballast) |  |  |  |  | 10 | €/m²
| PV array including inverter, cables, and meter of power sold to grid (ca. 10 m²) |  |  |  |  | 3250 | €/kWp
| PV array including inverter, cables, and meter of power sold to grid (ca. 200 m²) |  |  |  |  | 2750 | €/kWp
| Roof sealing for photovoltaics including inverter, cables, etc. (ca. 200 m²) |  |  |  |  | 3000 | €/kWp
450 | Telecommunications and information technology systems
460 | Conveyance systems
470 | - 490 Other technical systems

## 4. Heating demand
4a) | Indoor target temperature
| Hallways, stairwells, equipment rooms |  |  | 12 | °C
| Toilets, ancillary administration rooms |  |  | 15 | °C
| Gymnasiums, workshops, kitchens |  |  | 18 | °C
| Quiet areas |  |  | 18 | °C
| Offices and meeting rooms |  |  | 20 | °C
| Classrooms and common rooms in kindergartens |  |  | 20 | °C
| Changing rooms, washrooms, and showers |  |  | 22 | °C
4b) | Parameters for windows |  | U value | g value
| (k-value incl. frame) |  | (W/m²K) | (-)
| Single glazing |  | 5.2 | 0.8
| Insulating double glazing |  | 3 | 0.7
| Insulating triple glazing |  | 2 | 0.6
| Insulating double glazing |  | 1.4 | 0.62
| Insulating triple glazing |  | 0.9 | 0.55
4c) | Typical air exchange figures |  | Air exchange rate
| Schools, kindergartens, and retirement homes |  | 0.6 | 1/h
| Administration buildings |  | 0.8 | 1/h
| Residential buildings |  | 0.5 | 1/h
4d) | Heat from people
| Adults |  | 100 | W/P
| Children |  | 60 | W/P
| Average (residential) |  | 80 | W/P
4e) | Reduction factor shading and dirt
| exposed | fb= | 0.8
| protected area | fb= | 0.6
4f) | Global insolation | horizontal | South | East | West | North
| (Geisenheim) | 331 | 353 | 212 | 217 | 121 | kWh/m²a*
4g) | Limit and target values |  |  | Limit value | Target value
| For specific heating demand: |  |  | kWh/m²a | kWh/m²a
I | Single-family homes and duplexes |  |  | 85 | 60
II | Complexes, hotels, retirement homes |  |  | 75 | 50
III | Administrative buildings, schools, libraries |  |  | 75 | 50
Commercial buildings, simple stores, museums
IV | Inventories, gymnasiums, workshops |  |  | 60 | 40
Vehicle depots, train stations
V | Lecture halls, labs, laundries, restoration |  |  | 85 | 60
Hospitals, pools, theaters
Source: Leitfaden Heizenergie im Hochbau des Landes Hessen, HMUEJFG 1999

## 4.1 Standard use
Standard usage data
Usage type code |  |  | A | B | c | d | e | F | G | H | I | J | K | l | m | N | O | P | Q | R | s
Usage type |  |  | Single-family home | Multi-family complex | Retirement homes/hostels | Administration | Data centers | Standby services | Schools (general) | Elementary schools | Vocational schools | Day care centers | Gymnasiums | Pools** | Lecture halls/stages | Laboratory buildings | Hospitals | Care centers | Production plants/workshops | Stores | Warehouses
Share of usage days in heating season |  | NTH | 100% | 100% | 100% | 68.6% | 68.6% | 100% | 52.09% | 52.09% | 52.09% | 68.6% | 52.09% | 82.88% | 70.75% | 68.6% | 100% | 68.6% | 68.6% | 75.74% | 68.6% | [-]
Usage hours per usage day |  | NST | 15 | 15 | 18 | 10 | 10 | 24 | 10 | 6 | 10 | 10 | 12 | 12 | 14 | 10 | 24 | 8 | 10 | 12 | 10 | [h/d]
average number of people during use |  | PBN | 45 | 35 | 30 | 25 | 35 | 25 | 10 | 10 | 20 | 10 | 20 | 20 | 70 | 35 | 35 | 20 | 50 | 50 | 100 | [m²/P]
average indoor air temperature on days of use |  | TN | 20 | 20 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 22 | 20 | 20 | 22 | 20 | 18 | 20 | 16 | [°C]
average indoor air temperature on days without use |  | TL | - | - | - | 15 | 15 | - | 15 | 15 | 15 | 15 | 10 | 15 | 15 | 15 | - | 15 | 10 | 15 | 10 | [°C]
Heating limit temperature |  | TG | 12 | 12 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 15 | 12 | 12 | 12 | 12 | [°C]
with natural ventilation (windows and cracks):
average air exchange during usage |  | NLN | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.6 | 1 | 0.6 | 1 | 1 | 1 | 0.4 | [1/h]
average air exchange outside usage |  | NLL | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.2 | 0.2 | 0.6 | 0.2 | 0.2 | 0.2 | 0.2 | [1/h]
With mechanical ventilation:
mechanical air exchange during use (average) |  | MLN | 0.5 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.8 | 0.6 | 0.8 | 0.8 | 0.8 | 0.2 | [1/h]
mechanical air exchange during use (average) |  | MLL | 0.5 | 0.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.6 | 0 | 0.2 | 0 | 0 | [1/h]
Remaining air exchange from leaks (without pressure test) |  | RLOD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [1/h]
Remaining air exchange from leaks after successful pressure test* |  | RLMD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [1/h]
Data basis for supply of internal heat
Power consumption | pro m² ERA (without air conditioning) | SV |  |  |  | 25 | 50 | 25 | 15 | 10 | 20 | 15 | 15 | 15 | 25 | 50 | 40 | 200 | 50 | 50 | 10 | [kWh/(m²a)]
| per person |  | A: 1000; B: 1000; c: 1000 | [kWh/(P*a)]
Cold water consumption per person and day |  | KW | 100 | 100 | 100 | 15 | 15 | 15 | 15 | 10 | 20 | 15 | 15 | 15 | 15 | 50 | 100 | 20 | 50 | 5 | 0 | [l/(P*d)]
Hot water consumption per person and date (at 60°C) |  | WW | 34 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 30 | 0 | 25 | 30 | 20 | 0 | 0 | 0 | [l/(P*d)]
heat emitted from people per capita on average |  | WP | 80 | 80 | 80 | 100 | 100 | 100 | 80 | 60 | 80 | 80 | 200 | 200 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | [W]
Reduction factor electricity |  |  | 0.7 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | [-]
Heating of cold water |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 6 | 3 | 3 | 6 | 6 | [K]
Internal heat input during heating season (average)
Electrical appliances |  |  | 1.78 | 2.28 | 2.66 | 2.57 | 5.14 | 2.57 | 1.54 | 1.03 | 2.05 | 1.54 | 1.54 | 1.54 | 2.57 | 4 | 3.2 | 15.98 | 5.14 | 5.14 | 1.03 | [W/m²]
Persons |  |  | 1.11 | 1.43 | 2 | 1.14 | 0.82 | 4 | 1.74 | 0.78 | 0.87 | 2.29 | 2.6 | 4.14 | 0.59 | 0.82 | 2.86 | 1.14 | 0.57 | 0.76 | 0.29 | [W/m²]
Cold water drainage |  |  | -0.64 | -0.83 | -0.97 | -0.17 | -0.12 | -0.17 | -0.44 | -0.29 | -0.29 | -0.44 | -0.22 | -0.22 | -0.06 | -0.21 | -0.83 | -0.15 | -0.15 | -0.03 | 0 | [W/m²]
Hot water supply |  |  | 0.69 | 0.88 | 1.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 0 | 0.52 | 0 | 0.91 | 1.09 | 0 | 0 | 0 | 0 | [W/m²]
Evaporation |  |  | -0.43 | -0.56 | -0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.55736 | 0 | 0 | 0 | 0 | [W/m²]
average output total |  |  | 2.5 | 3.2 | 4.1 | 3.5 | 5.8 | 6.4 | 2.8 | 1.5 | 2.6 | 4.7 | 3.9 | 6 | 3.1 | 5.5 | 5.8 | 17 | 5.6 | 5.9 | 1.3 | [W/m²]
Average internal heat input on 230 heating days |  |  | 13.8 | 17.664 | 22.632 | 19.32 | 32.016 | 35.328 | 15.456 | 8.28 | 14.352 | 25.944 | 21.528 | 33.12 | 17.112 | 30.36 | 32.016 | 93.84 | 30.912 | 32.568 | 7.176 | [kWh/(m²a)]
Heating energy demand
Building category |  |  | I | II | II | III | III | III | III | III | III | III | IV | V | V | V | V | III | III | III | IV
Limit value |  |  | 85 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 60 | 85 | 85 | 85 | 85 | 75 | 75 | 75 | 60 | [kWh/(m²a)]
Target value |  |  | 70 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 70 | 70 | 70 | 70 | 55 | 55 | 55 | 45 | [kWh/(m²a)]
*) Air exchange at 50 Pa no greater than 1 1/h; **) without waste heat from pool water
with natural ventilation (windows and cracks):
average natural air exchange during heating season |  |  | 0.6 | 0.6 | 0.6 | 0.42866 | 0.42866 | 1 | 0.37363 | 0.30418 | 0.37363 | 0.42866 | 0.20418 | 0.26577 | 0.36509 | 0.42866 | 0.6 | 0.38293 | 0.42866 | 0.50296 | 0.25717 | [1/h]
With mechanical ventilation:
average mechanical air exchange during heating season |  |  | 0.5 | 0.5 | 0.6 | 0.22866 | 0.22866 | 0.8 | 0.17363 | 0.10418 | 0.17363 | 0.22866 | 0.10418 | 0.16577 | 0.16509 | 0.3715 | 0.6 | 0.18293 | 0.3715 | 0.30296 | 0.057165 | [1/h]

## 5. Heating capacity utilization
5a) | Demand for energy for hot water
(rough estimates)
| Residential | 600 | kWh/Pa
| Schools and kindergartens | 50 | kWh/Pa
5b) | U*-value of pipes |  |  | (heat conductivity = 0.035 W/mK)
| Pipe diameter DN | (mm) | 15 | 20 | 25 | 32 | 40 | 50 | 100
|  | (inches) | 1/2" | 3/4" | 1" | 5/8" | 1 1/2" | 2" | 4"
| Insulation in EnEV (mm) |  | 20 | 20 | 30 | 30 | 40 | 50 | 100
| U*-value | (W/mK) | 0.18 | 0.207 | 0.194 | 0.224 | 0.208 | 0.211 | 0.21
| Insulation in guidelines (mm) |  | 40 | 40 | 50 | 50 | 60 | 60 | 100
| U*-value | (W/mK) | 0.132 | 0.149 | 0.151 | 0.171 | 0.168 | 0.191 | 0.21
5c) | Siegert’s formula (sigma)
| Oil | 0.58 | 1/K
| Gas | 0.48 | 1/K
5d) | Standby losses |  | Output | Up to | 1978 | From 1979, not floating |  | From 1997, floating
| of boilers |  | (kW) | qB* | qB** | qB* | qB** | qB* | qB**
| Boiler with atmospheric burner |  | <50 | 0.04 | 0.05 | 0.02 | 0.03 | 0.015 | 0.02
| or ventilation burner |  | 50-120 | 0.03 | 0.04 | 0.015 | 0.025 | 0.01 | 0.013
| (VDI 2067) |  | 120-350 | 0.02 | - | 0.01 | - | - | -
|  |  | 350-1500 | 0.014 | 0.019 | 0.01 | - | - | -
qB* for simple burners and burners with instantaneous heaters without tanks
qB** for burners with hot water storage
5e) | Capacity utilization of central heating systems (oil/gas) |  |  |  |  | Limit value | Target value
| Heating system without service water heating |  |  |  |  | 0.85 | 0.9
| Heating system with service water heating only during heating season |  |  |  |  | 0.8 | 0.9
| Heating system with service water heating around the year |  |  |  |  | 0.75 | 0.85
Source: Leitfaden Heizenergie im Hochbau des Landes Hessen, HMUEJFG 1999
5f) | Gas prices (gross) |  | Business
| Prices from 01/2011 |  | Guarantee
| kWh rate |  | 0.06299 | €/kWh
5g) | District heat prices (gross) |  | Steam | Heat
| Prices from 01/2011 |  | Thermo D | Classic
| Output price |  | 19.86 | 22.51 | €/kW,a
| kWh rate |  | 0.0676 | 0.0774 | €/kWh
current prices at www.mainova.de, etc.
5h) | CO2 emissions for 1 MWh final energy |  |  | CO2
| (global CO2 equivalent) |  |  | (kg/MWh)
| Natural gas |  |  | 242
| District heat (70% cogen, hard coal) |  |  | 218
| Heating oil EL |  |  | 310
Source: www.gemis.de

## 6. Power demand
6a) | Full load hours, limit and target values for lighting
| Usage type | Usage | Nominal illuminance | Daylight | Usage | Full load | Full load | Limit value | Target value
|  | time | intensity | usage1) | Frequency | einfach2) | improved
|  | (h/a) | (lux) |  |  | (h/a) | (h/a) | (kWh/m²a) | (kWh/m²a)
| Office | 2700 | 300 | usually | constantly | 1000 | 500 | 10 | 3.5
|  |  | 500 | partly | constantly | 1500 | 1100 | 22 | 12
|  |  | 500 | without | constantly | 2750 | 2400 | 40 | 25
| Open-plan office |  | 750 | without | constantly | 2750 | 2400 | 55 | 35
| Schoolroom | 2000 | 300 | usually | often | 750 | 400 | 7.5 | 3
|  |  | 500 | partly | often | 1000 | 750 | 15 | 8
|  |  | 500 | without | often | 2000 | 1800 | 30 | 20
| Gymnasium | 2000 | 300 | partly | often | 1000 | 750 | 10 | 5.5
| Restaurant | 3600 | 200 | usually | often | 2000 | 1700 | 9 | 6
|  |  | 200 | partly | often | 3000 | 2000 | 13 | 7
|  |  | 200 | without | often | 3600 | 3300 | 16 | 11
| Transit areas | 2750 | 100 | usually | often | 1000 | 500 | 4.5 | 1.8
|  |  | 100 | without | often | 2750 | 2400 | 12 | 8
| Warehouse | 2750 | 100 | without | seldom | 500 | 300 | 2.2 | 1
|  |  | 100 | without | often | 1000 | 750 | 4.5 | 2.5
|  |  | 100 | without | constantly | 2750 | 2200 | 18 | 11
| Workshop | 2750 | 300 | usually | constantly | 1000 | 500 | 10 | 3.5
|  |  | 300 | partly | constantly | 1500 | 1100 | 15 | 8
| Parking garage | 2750* | 100 | without | often | 2750 | 2200 | 12 | 7.5
|  | 6500** | 100 | without | often | 6500 | 5500 | 28 | 18
1) | Usually: room depth < 5m ratio of glazing to floor area> 30 %
Partly: room depth > 5m ratio of glazing to floor area < 30 %
2) | simple: without lighting control, improved: with lighting control
* | Parking garage in office and commercial buildings
** | public parking garage
6b) | Nominal illumination and specific nominal output (rough estimates)
| Type of room usage |  | Lighting | sp. output | sp. output
|  |  | intensity | simple | improved
|  |  | (lux) | (W/m²) | (W/m²)
| Transit paths in buildings |  | 100 | 2.5 | 2
Hallways, stairwells, entrance halls
Storage rooms with search areas
Theaters (audience room)
Homes
| Cafés, restaurants, cafeterias |  | 200 | 5 | 4
Warehouses with reading areas
| Individual offices with windows (D > 1%) |  | 300 | 7.5 | 6
School rooms, libraries
Conference rooms
| Offices without windows (D < 1%) |  | 500 | 12.5 | 10
Special teaching rooms
Kitchens, workshops
Exhibition and trade show halls
6c) | Limit and target values for ventilation and air-conditioning
| Usage type | Usage | Persons | average | additional | Limit value | Target value | Examples
|  | time | occupancy | Heat, electric | Usage
|  | (h/a) | (m²/P) | (W/m²) |  | (kWh/m²a) | (kWh/m²a)
| Window ventilation |  |  |  |  | 0 | 0
without cooling
| Office | 2700 | 15 | <20 | non-smoking | 3 | 1.5 | office with normal
|  |  | 15 | <20 | smoking | 7.5 | 3 | tactical equipment
|  |  | 10 | 30 | non-smoking | 12 | 6 | Office with a lot of
| Open-plan office |  | 10 | 30 | smoking | 18 | 7.5 | equipment
| Schoolroom | 2000 | 7 | <20 | non-smoking | 4.6 | 1.5 | normal schoolroom
|  |  | 10 | 30 | non-smoking | 9 | 3.6 | a lot of equipment exercise room
|  |  | 3 | 40 | non-smoking | 18 | 6 | lecture hall
| Restaurant | 3600 | 2 |  | 50% smoking | 15 | 4.2 | low occupancy
|  |  | 1.2 |  | 50% smoking | 24 | 9 | average occupancy
| Transit areas | 2750 |  |  | 15m³/m²h | 9 | 3 | wardrobe, sanitation room
| Warehouse | 2750 |  |  | seldom used | 1.5 | 0.7 | archive
[5 empty] | often used | 3 | 1.5 | sales warehouse
[5 empty] | often gel. | 15 | 6 | delivery of sensitive goods
| Workshop | 2750 |  |  | 15 m³/m²h | 18 | 6 | special requirement for
pollutants or heat dissipation
| Parking garage | 2750* |  |  | 2 m³/m²h | 1.5 | 0.9 | Parking garage office
|  | 6500** |  |  | 3m³/m²h | 3.6 | 1.5 | public parking garage
6d) | Rough estimates for full load hours ventilation
| Usage type | Usage | Conditions of use |  | Full load | Full load
|  | time |  |  | simple | improved
|  | (h/a) |  |  | (h/a) | (h/a)
| Office | 2750 | Mechanical ventilation |  | 2750 | 2000
| Schoolroom | 2000 | school and exercise rooms |  | 2000 | 1200
|  |  | Lecture halls and conference rooms |  | 1500 | 500
| Restaurant | 3600 | Mechanical ventilation |  | 1000 | 700
| Transit areas | 2750 | wardrobe, sanitation room |  | 1000 | 500
| Warehouse | 2750 | seldom used |  | 1000 | 600
|  |  | often used |  | 1500 | 1000
|  |  | requires constant ventilation |  | 8760 | 5500
| Workshop | 2750 | requirement pollutants or heat dissipation |  | 2000 | 1000
| Parking garage | 2750 | Office buildings |  | 1500 | 1000
|  | 6500 | public parking garages |  | 2000 | 1200
6e) | Rough estimates for full load cooling
| Usage type | Usage | average | Full load | Full load
|  | time | Heat, electric | simple | improved
|  | (h/a) | (W/m²) | (h/a) | (h/a)
| Office | 2750 | 30 | 550 | 400
|  |  | 40 | 800 | 600
| Schoolroom | 2000 | 30 | 400 | 250
|  |  | 40 | 600 | 350
| Sales | 3600 | 30 | 650 | 400
|  |  | 40 | 1000 | 600
6f) | Limit values for auxiliary energy for heating
For new buildings and renovations with
| improved insulation |  | 0.8 | kWh/m²a
For renovations without improvements
| to insulation |  | 1% | *
*of the average energy demand for heating and hot water
Source: Leitfaden Elektrische Energie im Hochbau des Landes Hessen, HMULF 2000
6g) | Rough averages
| Rough average for PC workstation |  | 80 | W
| PC without screen |  | 50 | W
| 17-inch monitor on standby |  | 0 | W
| 17-inch monitor in use |  | 70 | W
| 17-inch TFT monitor on standby |  | 2.3 | W
| 17-inch TFT monitor in use |  | 31 | W
| laser printer standby |  | 11 | W
| laser printer operation |  | 200 | W
| inkjet printer standby |  | 2.5 | W
| inkjet printer operation |  | 50 | W
| scanner standby |  | 18 | W
| scanner operation |  | 23 | W
| projector standby |  | 5.4 | W
| projector operation |  | 190 | W
6h) | Power prices (gross) |  | Business | Business | Business
| Prices from 01/2011 |  | Power 2 | Highpower 1 | Highpower 2
| Output price |  | 109.1 | 97.41 | 165.51 | €/kW,a
| kWh high tariff |  | 0.2067 | 0.1852 | 0.1786 | €/kWh
| kWh low tariff |  | 0.2067 | 0.1852 | 0.1282 | €/kWh
current prices at www.mainova.de, etc.

## 7. Water demand
7a) | Flush volume/flow volume
| Old toilet tank | 6 - 9 | l
| Target toilet tank | 4,5 | l
| Old urinals | 2 - 4 | l
| Target urinals | 0 | l
| Old sinks | 6-10 | l/min
| Target sinks | 5 | l/min
| Old shower | 9-12 | l/min
| Target shower | 7 | l/min
7b) | Flushing frequency toilets/urinals
| (flushes per person and day) | Excrement | Urin
| Usage type | (flush/P*d) | (flush/P*d)
| Administration | 1 | 2
| School/kindergarten | 0.5 | 1.5
| Gymnasiums/sports facility/pool | 0 | 1
7c) | Service life*
| Sink, administration | 2 | min/P,d
| Sink, school/kindergarten | 1,5 | min/P,d
| Sink, gymnasium/sports facility | 0,8 | min/P,d
| Showers, school | 0,01 | min/P,d
| Showers, gymnasium, sports facility (sports club) | 5 | min/P,d
| Showers, pools | 8 | min/P/d
*25 percent less with self-closing taps
7d) | Flow lawful rate for roofs
| Roof type | W
| Gabled roof: tiles/concrete stones | 0.75
| Flat roof: gravel, bitumen | 0.6
| Green roof | 0.3
7e) | Water prices (gross) | Mainova
| Prices from 01/2011 | Classic
| Price of water | 2.01 | €/m³
| Sewage connection | 1.76 | €/m³
current prices at www.mainova.de, etc.